## Slide 1: “Examination of VVER fuel behaviour under severe accident conditions, Quench state” Status report on the ISTC project # 1648.2
Presented by A. Goryachev,
RIAR, Dimitrovgrad, Russia
12 CEG-SAM Meeting September 11-13, 2007 St. Petersburg 1

## Slide 2
Determination of FP release
Quench
tank
Ar carrier gas
Ar, 85Kr, Xe
g - detector
MFM
mass-spectrometer
Ar carrier gas
Gamma - spectrum
Gas flow rate
Xe concentration
85Kr and Xe release rate
85Kr activity
12 CEG-SAM Meeting September 11-13, 2007 St. Petersburg 2

## Slide 3
Reflood temperature, °С Oxide film thickness, m | 1400 | 1600 | 1700
0 | 2 | 2 | 2
100 | 2 | 1 | 
300 |  |  | 
Tests performed in the frame of stage A Spent ROD-QUENCH Project “Examination of the VVER fuel behavior under the severe accidents. Reflooding stage "
12 CEG-SAM Meeting September 11-13, 2007 St. Petersburg 3
1

## Slide 4: Tests with irradiated simulators quenched without pre-oxidation
12 CEG-SAM Meeting September 11-13, 2007 St. Petersburg 4
Simulator #37
No preliminary oxidation
Annealing within 240 s in argon at 1400 °C to get data for comparative analysis of gaseous fission product release kinetics
Quenching at 1700 °C
Simulator was broken during handling immediately after the test

## Slide 5: Tests with irradiated simulators quenched with pre-oxidation
Simulator #39
Pre-oxidation time at 1400 °C is 240 s
Quenching at 1400 °C
Simulator was broken during post-test examinations
12 CEG-SAM Meeting September 11-13, 2007 St. Petersburg 5

## Slide 6
Simulator #51 (1600 оС, oxidized 100 µm)
12th CEG-SAM Meeting September 11-13, 2007 Saint Petersburg

## Slide 7
Simulator #51 (1600 оС, oxidized 100 µm)
12th CEG-SAM Meeting September 11-13, 2007 Saint Petersburg

## Slide 8: Results of the irradiated simulator tests
12 CEG-SAM Meeting September 11-13, 2007 St. Petersburg 8
Test # | 36 | 37 | 39 | 40 | 45 | 46 | 47 | 49 | 51
Fuel Burnup, MW·d/kgU | 54 | 54 | 65 | 65 | 65 | 65 | 65 | 65 | 65
Pre-oxidation (annealing) time at 1400 °C, s | 240 | 0 | 240 | 0 | 240 | 240 | 240 | 240 | 240
Simulator environment | steam-Ar | Ar | steam-Ar | Ar | Ar | Ar | Ar | Ar | steam-Ar
Quench temperature, °C | 1400 | 1700 | 1400 | 1400 | 1600 | 1400 | 1600 | 1700 | 1600
Maximum temperature during the quench, °C | 1407 | 1703 | 1428 | 1411 | 1604 | 1422 | 1604 | 1706 | 1658
Total hydrogen production, mg | 164 ± 13 | 16.3 ± 1.3 | 173 ± 14 | 13.6 ± 1.1 | 20.6 ± 1.6 | 9.4 ± 0.6 | 20.4 ± 1.6 | 25.9 ± 2.0 | 208 ± 16
Hydrogen production during the quench, mg | 6.7 ± 0.5 | 14.7 ± 1.2 | 7.0 ± 0.6 | 13.6 ± 1.1 | 20.6 ± 1.6 | 9.4 ± 0.6 | 19.3 ± 1.5 | 23.4 ± 1.9 | 21.1 ± 1.7

## Slide 9
Determination of relative release of volatile FP
Relative method.
Test 36 (Burnup 54 MWd/kg U;
isothermal annealing: 1400°C, 240 s; quenching temperature 1400 °C)
12 CEG-SAM Meeting September 11-13, 2007 St. Petersburg 9

## Slide 10
Determination of initial content of 85Kr and Xe
The content of 85Kr and Xe in the reference sample is assumed as the initial 85Kr specific activity Аref and initial specific volume of the xenon VXe ref and calculated on the basis of the results of the experiment on dissolution of the fuel reference sample.
fuel sample at moving bowl
mass flow meter
bubblers
mass spectrometer
Ar
TC
heater
dissolution device
filter
Ge(Li) - detector
mass flow controller
Hot cell
Rig for determination of FP content by fuel dissolution
MS

P 1
Ar
MS
MFM
MFC
dump
filter
12 CEG-SAM Meeting September 11-13, 2007 St. Petersburg 10

## Slide 11
Determination of Cs relative release
The parameters determined :
volumetric activity and radionuclide composition in quench tank water;
- specific activity and radionuclide composition of the acid solution (reference fuel specimen or tested sample);
Relative error of activity determination is 9% (Р=0,95).
Test
solution
Volume measurement
Remote probe sampling
g - spectrometry
Probe
dilution
g - detector
134Cs, 137Cs activity
12 CEG-SAM Meeting September 11-13, 2007 St. Petersburg 11

## Slide 12
FP release calculated using the dissolution results
Test | 36 |  | 37 | 39 |  |  | 40 |  | 
Burnup, МWd/kg U | 54 |  | 54 | 65 |  |  | 65 |  | 
Holding time at 1400°С, s | 240 |  | 240 | 240 |  |  | 0 |  | 
Maximal temperature, °C | 1400 |  | 1700 | 1400 |  |  | 1400 |  | 
85Kr release (on-line measurement), % | 18.1±4.0 |  | 31.8±3.2 | 8.4±4.5 |  |  | 4.1±4.5 |  | 
137Cs release calculated using -scanning data, % | 5 |  | - | 9 |  |  | 3 |  | 
Sample position along the simulator, mm | 90 | 22 | 96 | 131 | 95 | 11 | 136 | 84 | 19
85Kr release calculated by dissolution data, % | 18.8 ± 4.0 | 2,0 ± 5.0 | 42,3 ± 2.7 | 16,9 ± 4.1 | 12,7 ± 4.3 | 8,2 ± 4.5 | 9,9 ± 4.5 | 2,2 ± 4.8 | 2,3 ± 4.8
137Cs release calculated by dissolution data, % | 8,2 ± 9,2 | <2 | 37,8 ± 6,2 | 6.0 ± 9,4 | 5,4 ± 9,5 | 3,0 ± 9,7 | 7,5 ± 9,3 | <2 | <2
Measured 85Kr concentration in the reference samples: 54 МWd/kg U– 3.5 μl/g
65 МWd/kg U– 6.6 μl/g
12 CEG-SAM Meeting September 11-13, 2007 St. Petersburg 12

## Slide 13
Simulator test parameters and FP release
12 CEG-SAM Meeting September 11-13, 2007 St. Petersburg 13
Test |  | 36 | 37 | 39 | 40 | 42* | 43** | 45 | 46 | 47 | 49 | 51
Burnup, МWd/kgU |  | 54 | 54 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65
Holding time at 1400°С, s |  | 240 | 240 | 240 | 0 | 0 | 340 | 240 | 240 | 240 | 240 | 240
Quench temperature, °C |  | 1400 | 1700 | 1400 | 1400 | 1600 | 1400 | 1600 | 1400 | 1600 | 1700 | 1600
Total 85Kr release, μl STP |  | 37 ± 4 | 65 ± 8 | 33 ± 4 | 16 ± 2 | 29 ± 4 | - | 18 ± 2 | 11 ± 1 | 16 ± 2 | 28 ± 3 | 19 ± 2
Total Xe release, ml STP |  | 12.9 ± 1.3 | 34 ± 3.4 | 9.9 ± 1.0 | 4.9 ± 0.5 | 15.4 ± 1.6 | - | 5.0 ± 0.5 | 3.1 ± 0.3 | 4.9 ± 0.5 | - | -
Relative 85Kr release, % |  | 18.1 ± 4.0 | 31.8 ± 3.2 | 8.4 ± 4.5 | 4.1 ± 4.5 | 7.4 ± 4.5 | - | 5.1 ± 4.5 | 3.1 ± 4.6 | 4.2 ± 4.5 | 7.6 ± 4.5 | 5.2 ± 4.5
Relative 85Kr release from simulator central part (dissolution data), % |  | 18.8 ±4.0 | 42,3 ±2.7 | 12,7 ±4.3 | 2,2 ±4.8 |  |  |  |  |  |  | 
Cs release in the cooling tank water, % | 137Cs | 0.6 ±0.2 | 1.2 ±0.3 | 1.3 ±0.3 | 0.6 ±0.2 | 0.8 ±0.2 | 1.2 ±0.3 | 0.9 ±0.2 | 0.4 ±0.2 | 1.1 ±0.3 | - | 0.8 ±0.2
 | 134Cs | 0.5 ±0.2 | 1.0 ±0.2 | 1.2 ±0.3 | 0.6 ±0.2 | 0.9 ±0.2 | 1.2 ±0.3 | 0.9 ±0.2 | 0.4 ±0.2 | 1.1 ±0.3 | - | 0.8 ±0.2

## Slide 14
Summary
12 CEG-SAM Meeting September 11-13, 2007 St. Petersburg 14
The progress in tests performance have been achieved after repair of installation.
Data on volatile FP content in samples of initial fuel are obtained
Tests with dissolution of the initial and tested samples have shown that the used method can be applied to the simulators tested at temperatures of 1700 оС. At lower temperatures (1400 оС) the error exceeds the result

## Slide 15
Part 2. Application of the SVECHA/QUENCH and MFPR codes to simulation of
the RIAR quenching tests
with VVER irradiated fuel rods

## Slide 16
Crack formation in RIAR tests with irradiated fuel rod simulators
Group | Test # | Initial temp. | Outer ZrO2 | Outer Zr(O) | Inner Zr(O) | Inner ZrO2 | State of the cladding after the test
 |  | °С | m | m | m | m | 
I | 36 | 1400 | 111 | 186 | 170 | - | Intact.
 | 39 | 1400 | 92 | 126 | 122 | 27 | Intact. Broken during handling.
 | 43 | 1400 | - | - | - | - | Intact. Broken during handling.
II | 40 | 1400 | 9 | 23 | 90 | 10 | Intact.
 | 46 | 1400 | - | - | - |  | Intact.
 | 42 | 1450* | - | - | - | - | Intact. Broken into 2 parts during handling.
 | 45 | 1600 | - | - | - | - | Intact. Broken into 2 parts during handling.
 | 37 | 1700 | 19 | 31 | 337 | 0 | Intact. Broken into 2 parts during handling.

## Slide 17
Simulation of the RIAR quench tests with irradiated fuel rod simulators (1/3)
Test #36
Layers thickness, m
Elevation, mm | Measurement |  | Simulation | 
 | Outer Zr(O) | Outer ZrO2 | Outer Zr(O) | Outer ZrO2
127 | 162 | 108 | 161 | 111
77 | 186 | 111 | 158 | 113
27 | 47 | 51 | 157 | 112
Test ID | Measurement |  | Simulation | 
 | Total | Quench | Total | Quench
36 | 165.0 | 6.7 | 129.5 | 0.2
39 | 173.2 | 7.1 | 126.9 | 0.2
40 | 13.6 | 13.6 | 12.6 | 12.6
Hydrogen release, mg

## Slide 18
Simulation of the RIAR quench tests with irradiated fuel rod simulators (3/3)
Comparison of the calculated and measured temperatures in the pellet centre at elevation 77 mm during quenching.
Hydrogen release, mg
Test #40
Layers thickness, m
Measurement |  | Simulation | 
Total | Quench | Total | Quench
13.6 | 13.6 | 12.6 | 12.6
Elevation, mm | Measurement |  | Simulation | 
 | Outer Zr(O) | Outer ZrO2 | Outer Zr(O) | Outer ZrO2
127 | - | - | 18 | 13
77 | 23 | 9 | 19 | 14
27 | 5 | 6 | 11 | 8

## Slide 19
Simulation of the RIAR quench tests with irradiated fuel rod simulators (2/3)
Comparison of the calculated and measured temperatures in the pellet centre at elevation 77 mm during quenching.
Hydrogen release, mg
Elevation, mm | Measurement |  | Simulation | 
 | Outer Zr(O) | Outer ZrO2 | Outer Zr(O) | Outer ZrO2
127 | 151 | 101 | 163 | 106
77 | 126 | 92 | 160 | 108
27 | 58 | 39 | 162 | 110
Test #39
Layers thickness, m
Measurement |  | Simulation | 
Total | Quench | Total | Quench
173.2 | 7.1 | 126.9 | 0.2

## Slide 20
MFPR code simulation of the RIAR quench tests with irradiated fuel
Test # 36 (53.5 MWd/kgU)
Test # 40 (65 MWd/kgU)
Test # 39 (65 MWd/kgU)
Test # | Experiment | MFPR calculation
36 | 4.6 | 6.4
39 | 8.8 | 7.1
40 | 2.6 | 4.1
Cs fractional release, %

## Slide 21
Conclusions on the modelling of RIAR tests
SVECHA/QUENCH (S/Q) and MFPR codes were adapted to simulate behaviour of the VVER fuel rod simulators in the RIAR quenching tests.
The modified S/Q code well predicts the temperature evolution during quenching, the maximum extent of Zr-1%Nb cladding oxidation and the final mechanical state of the oxidized Zr-1%Nb cladding in the tests with fresh uranium fuel rods.
The S/Q code was extended for simulation of the RIAR quenching tests with irradiated fuel rods. Analysis and simulations of the tests show that the gap collapse and chemical interaction between the burned fuel pellets and the cladding due to swelling leads to additional embrittlement of the cladding.
The MFPR code reasonably predicts Cs release in the RIAR quenching tests with irradiated fuel rods.