## Slide 1: STATUS OF ISTC PROJECT # 3609: EXPERIMENTAL INVESTIGATION OF FLOW PULSATION EFFECTS ON BURNOUT IN RPV EXTERNAL COOLING SYSTEM (EXPULS)
Presented by S. Bechta 13th CEG -SAM Meeting
A.P. Alexandrov Research Institute of Technology

## Slide 2: Problem formulation (1)
  IVR concept is used in:
  - current projects (AP-600, АР - 1000, VVER - 640)
  - new-generation projects (APR - 1400)
  - modernization (VVER - 440)
  Absence of DNB at the vessel external cooling is critical for IVR

## Slide 3: Problem formulation (2)
Experimental data and correlations for CHF versus water mass velocity, subcooling and surface inclination angle are available for conditions of vessel external cooling
The CHF value can be affected by flow oscillations. This has been observed during DNB experiments with water boiling in pipes. This effect has not been studied yet for IVR
The factor causing oscillations growth is outlet hydraulic resistance to two-phase flow (e.g. slot channels, local hydraulic resistances etc.)

## Slide 4: Objectives
Quantification of flow oscillation influence on CHF at the external surface of reactor vessel

## Slide 5: NITI tests on DNB on the external surface of reactor vessel (1)
14 – water ; 5 – helium ; 6 – nitrogen ; 7 – (1)
- Kutateladze correlation
(1)
=180-
The effect of inclination angle
Saturated liquid

## Slide 6: NITI tests on DNB on the external surface of reactor vessel (2)
Forced circulation of coolant
Effects of mass velocity and subcooling were studied separately
Bottom model– slice-geometry, scale 1:1
“Hot spot” method
Test facility PETLYA
sink
distillate

## Slide 7: NITI tests on DNB on the external surface of reactor vessel (3)
1, 2, 3 – PETLYA ; 1– =0; 2 – =27; 3 – =90;
4 – ULPU; 5 – «Gidropress»; 6 – (2)
(2)
Generalization of CHF data
Effect of mass velocity and subcooling

## Slide 8: NITI tests on DNB on the external surface of reactor vessel (4)
Test section is the same as in PETLYA test facility
Natural circulation of coolant
Circuit height is 7m
Test facility KEDR

## Slide 9: NITI tests on DNB at the external surface of reactor vessel (5)
1 – forced circulation;
W=50…350 kg/(m2s); Р=0.14…0.17 MPа;
2 – natural circulation;
W=80…250 kg/(m2s); Р=0.15…0.17 MPа;
3 – open circulation circuit
qcr, MW/m2
-
0
.
1
2
-
0
.
1
0
-
0
.
0
8
-
0
.
0
6
-
0
.
0
4
-
0
.
0
2
0
.
0
0
0
.
5
0
1
.
0
0
1
.
5
0
2
.
0
0
2
.
5
0
-
1
-
2
-
3
X
=27
Comparison of CHF experimental data for forced and natural circulation

## Slide 10: Flow oscillations in the KEDR test facility
Subcooled water in the upper tank
Low-frequency oscillations
Flow oscillations are caused by periodical boiling evolution, flow rate increase, suppression of boiling with subcooled water, etc.
The process is well described in the KORSAR code
0
500
1000
1500
2000
0
1
2
3
4
5
0
500
1500
2000
350
360
370
380
390
KEDR
calc
exp
KEDR
calc
exp
exit
time, s
time, s
Temperature, K
Flow rate, kg/s

## Slide 11: Flow oscillation in the VVER- 440 vessel external cooling system (1)
Vessel cooling by gravity water flow

## Slide 12: Flow oscillation in the VVER- 440 vessel external cooling system (2)
Calculation results by using KORSAR code
G, kg/s
G, kg/s
t, s
t, s
G =28 kg/s
Flow reverse caused by volume boiling at the slot channel inlet
Detail

## Slide 13: Flow oscillations in the vessel external cooling system
Oscillations could reduce CHF value
Characteristics of oscillations depend on circuit geometry and coolant parameters

## Slide 14: Assets for EXPULS project
Model of VVER-1000 vessel bottom
KEDR test facility
KEDR transformability into the gravity water flow system
KEDR compatibility with existing KMS infrastructure
KORSAR computer code

## Slide 15: Project tasks
№ | Task | Pers*day
1 | Pretest calculations. Preparation of facility. Testing of experiment procedure. Refinement of experimental matrix | 1020
2 | Tests: DNB in natural circulation circuit | 1360
3 | Tests: DNB under gravity flow conditions | 1780
4 | Verification of computer codes | 1490
 |  | 5650

## Slide 16: Expected project results
Experimental data on CHF at flow pulsations
Correlations between the intensity of flow pulsations and the CHF value
Verification of RELAP5mod3.2 and KORSAR/В1.1 computer codes

## Slide 17: Application of results
Expansion of application area of RELAP and KORSAR computer codes
Verification of other thermal-hydraulic computer codes, for instance, CATHARE, ATHLET
Design of the systems for external cooling of reactor vessel
IVR analysis

## Slide 18: General project information
The project is carried out by NITI
Project manajer – Dr. Yu. Migrov
Participants – 20 persons including 13 weapon scientists (5 PGD) and engineers
Duration – 24 months
Requested funding – $ 184,000

## Slide 19: Conclusions
NITI has the experience of experimental studies of DNB and computer code application for modeling thermal hydraulics in vessel external cooling systems
EXPULS project will give an insight into DNB affected by flow oscillations