## Slide 1: Comments from E. Altstadt
The report on the calculation of VVER-440 scenarios which were performed so far should be made available to the collaborators. Which accident scenarios were selected? Description of the analysis (MELCOR calculations?)
The report on the creep tests performed so far should also be prepared. It should contain the test conditions (temperatures, stresses) and the creep curves, eventually Larsen-Miller parameters.
Generally it is recommended to elaborate half-yearly reports to give an detailed overview on the work performed and the results obtained

## Slide 2: Comments from E. Altstadt
Is the whole vessel made from RPV steel ? In order to save money MPEI should consider to manufacture only the “hot part” of the vessel from RPV steel (like it was done in the FOREVER program).
Is there in the meantime a solution for the missing money? If there is money available for only one test, I would suggest a test were the peak heat flux is in the cylindrical part of the vessel (corresponding to a high melt level)